Ogden City School District

Request for Proposal

Washington High School

Electrical / Telecommunications

RFP # RFP1-011

Surface Raceway, Cable Management,

End to End Category 6, 450 MHz System

1950 Monroe Blvd.

Ogden, Utah

January 25, 2011

Invitation for Proposals

Notice is hereby given that Ogden City School District is inviting proposals to provide services for Washington High School at 455 28th street,

Ogden, Utah 84401.

Telecommunications

- Category 6, 450 MHz Plenum cable, all horizontal lines

- Category 6, 450 MHz Patch Cables

- Hubbell Cat 6 patch panels

- Ladder rack support to wall is required for 2 and 4 post racks

- Hubbell category 6 modular jacks (Voice – Gray, Data - Black)

- Hubbell face plates to match raceway or equivalent

Bids will be received by the Board of Education of Ogden City School District.  Bids will be in accordance with specifications prepared by Technology Supervisor. Bids will be accepted for Telecommunications. Bid must list all Telecommunications line items with quantity and amounts separately.

The Ogden District requires bidding contractors to have Erate SPIN to participate.  This SPIN number must be included on sealed bid document.  This project will follow guidelines and timelines specific to the School and Libraries Division and contingent on all factors.

The Board of Education of Ogden City School District reserves the right to reject any or all bids or to waive any information or technicality in any bid in the interest of the District.  Contractor is liable for damage caused during installation.  The Board of Education of Ogden City School District reserves the right to terminate this project without cause.

A Pre-Bid walk through meeting will start at Washington High main office at 455 28th street, Ogden, Utah 84401, on February 8, 2011.  The meeting will start at 11:00 AM.  We will visit all rooms after initial meeting and attendance at walk through is mandatory to qualify to bid project.  Documents provided by Ogden District.

Sealed bids must be delivered no later than 2:00 pm Mountain Time March 1, 2011 and contain provided RFP number and SPIN.  Proposals will be accepted in the office of the Purchasing Director at the Ogden City School District Administration Building, Room 209, 1950 Monroe Blvd. Ogden, Utah 84401-0619.

  - Telecommunications Proposal

- Scope of work

1.	The contractor (Telecommunications) shall supply all labor and material for a complete functional system as described herein. It will include installing all cabling, conduit or surface molding, faceplates, boxes,  grounding cables, vertical wire management, rack mounted patch panels, modular jacks, racks, 2 meter category 6 450 MHz patch cables, 50 micron 24 strand fiber with LIU and SC termination.

2.	The contractor shall test, document and warranty system.

- Equipment

  - Hubbell horizontal wire management for MDF and IDF (6 each)

  - Hubbell category 6 patch panels

  - Hubbell category 6 modular jacks (RJ-45)

  - Labeling is required at technology closets (MDF, IDF) and all termination points. Patch panels and jacks.

  - 2 – 2 meter patch cables, category 6, 450 MHz, per horizontal cable

- System Requirements

  - All horizontal cabling will be category 6, 450 MHz plenum cable

  - Maximum horizontal run will be 295 feet

  - Follow the EIA/TIA 568B standard

  - Conduit and or surface molding (no exposed cabling in classrooms except patch cable to device).

  - Grounding cable to all racks

  - All equipment locations specified by Ogden School District Technology Supervisor or Network Engineer only.  No changes without their authorization.

  - Cable support must be provided to specifications in tunnels

  - Voice over Ethernet Jack must be Gray

  - Data Jack must be Black

  - Top left jack must be Gray

  - All Voice over Ethernet jacks must terminate on their own patch panel

  - Horizontal Cabling: Voice cables must have different color than data.

  - Each data jack location has conduit stubbed to wire type cable tray in hall.

  - Pull out old data line while installing new.

- Provide to all Classrooms

  - 10 new data drops per classroom

  - Provide two meter category 6 patch cables per data drop

- Provide to Computer Lab

  - Replace existing 36 data locations

  - Provide two meter category 6 patch cables per data drop

- Provide to Media Center and Lunch Area

  - Replace all existing data locations

  - Provide two meter category 6 patch cables per data drop

- Provide to all main office locations

  - Replace all existing data locations

  - Provide two meter category 6 patch cables per data drop

- Add 3 data drops to each hall location on drawing (8 locations)

  - Future IP camera and AP

  - Provide two meter category 6 patch cables per data drop

- Contact Information

  - Contact Ogden School District Technology Supervisor at dont@ogdensd.org or cell phone 801-430-1283

  - Alternate Contact:  Dustin Smith smithd@ogdensd.org