Ogden City School District

Request for Proposal

RFP # RFP1-013

Ben Lomond High School

Electrical / Telecommunications

RFP

Electrical Power, Surface Raceway,

Equipment Racks, Cable Management,

End to End Category 6, 450 MHz System

1950 Monroe Blvd.

Ogden, Utah

February 1, 2011

Invitation for Proposals

Notice is hereby given that Ogden City School District is inviting proposals to provide services for Ben Lomond High School (Rooms E209, E212, E222, and D215) at 1080 9th St., Ogden, Utah 84401.

Electrical

- Wiremold Evolution Series, Fire-Rated Poke-Through where required

- Must provide core drilling for poke-through

  - Rooms with carpet, contractor is responsible for cutting, cleaning, and sealing hole through carpet to accommodate poke-through

  - Exact location of poke through may vary.

  - Contractor must verify core drilling will not cause damage to structure

- Power for 38 computers each (4 computers per 20A 120V circuit) in room E209, E121, E222, and D215.

- Data for 38 Computers in each room.

- Power sub panel if required.  Must support future expansion.

Telecommunications

- Category 6, 450 MHz Plenum cable, all horizontal lines

- Category 6, 450 MHz Patch Cables

- Hubbell patch panels

- Hubbell horizontal wire management

- Hubbell category 6 modular jacks (Black)

- Data for 38 computers in room E209

- Data for 38 computers in room E212

- Data for 38 computers in room E222

- Data for 38 computers in room D215

Contractor is responsible for repairing any damage incurred as part of this proposal.

Contractor is responsible for cleanup as part of this proposal.

The Board of Education of Ogden City School District reserves the right to reject any or all bids or to waive any information or technicality in any bid in the interest of the District.

A Pre-Bid mandatory walk through meeting will be held at Data Center Conference room, 1080 9th St., Ogden, Utah 84401 on February 15, 2011.  The meeting will start at 9:00 AM.  We will visit the site after initial meeting and attendance at walk through is mandatory to qualify.

Sealed bids will be received by the Board of Education of Ogden City School District at Administration building room 209, 1950 Monroe Blvd. Ogden Utah 84401, March 8, 2011 by 2:00PM. No late bids will be accepted.  Bids will be in accordance with specifications prepared by Technology Supervisor. Bids will be accepted for combined Electrical and Telecommunications only. Contractor must provide subcontract work for areas outside company. The bid must list Electrical and Telecommunication amounts separately by room. Bids will be awarded after due date to include notification to all contractors participating in project.

Provide separate bids, one for each Room E209, E212, E222, and D215

Work for this project will start April 7, 2011 through April 11, 2011 there is no school.  If project not completed work must take place before, or after school, or on Saturdays.

  - Electrical / Telecommunications Proposal

- Scope of work

  - The contractor (Electrical and or Telecommunications) shall supply all labor and material for a complete functional system as described herein. It will include installing all cabling, conduit or surface molding, faceplates, boxes, 20A 120V circuits, sub panels, 6x6 Poke-Through, core drilling, grounding cables, vertical and horizontal wire management, rack mounted patch panels, modular jacks, 2 meter category 6 450 MHz patch cables.

- Ogden District will provide detailed documentation related to project.

- The contractor shall test, document and warranty system.

- Equipment

  - Wiremold Evolution Series, Fire-Rated Poke-Through.  Installs in a 6” diameter core drilled hole where required, no substitutes

  - Hubbell category 6 patch panels

  - Hubbell category 6 modular jacks (RJ-45)

  - Hubbell horizontal wire management (1 per patch panel)

  - Labeling is required at technology closets (MDF, IDF) and all termination points.

  - 60, category 6, 450 MHz, 2 meter patch cables for E209

  - 60, category 6, 450 MHz, 2 meter patch cables for E212

  - 60, category 6, 450 MHz, 2 meter patch cables for E222

  - 60, category 6, 450 MHz, 2 meter patch cables for D215

  - Four computers per one, 20A 120V circuit.

  - Connections to support 38 computers

  - Where new sub panel is required, up size for future expansion         (ex:  200 Amp panel)

- System Requirements

  - All horizontal cabling will be category 6, 450 MHz plenum cable

  - Maximum horizontal run will be 295 feet

  - Follow the EIA/TIA 568B standard

  - Conduit and or surface molding (no exposed cabling to classrooms except patch cable to device).

  - All equipment locations specified by Ogden School District Technology Supervisor or Network Engineer only.  No changes without their authorization.

  - Cable support must be provided to specifications in tunnels or ceiling areas.

- Room Requirements

  - 4 - Wiremold Evolution series poke through with 6 power outlets and 6 data jacks.

  - 3 - Wiremold Evolution series poke through with 4 power outlets and 4 data jacks.

  - 1 - Wiremold Evolution series poke through with 2 power outlets and 2 data jacks.

  - Approximate location of poke through provided by Ogden District

  - Exact core drill location determined by contractor.

- Contact Information

  - Contact Ogden School District Technology Supervisor at dont@ogdensd.org: Phone 801-737-8815